## General_Registers
Label | Category | Start | End | Size | Address | Access Level | NV | Type | Range | Default | Units | Description
RRCR State | RRCR Power Reducer | 0 | 0 | 1 | F800 | R | - | Uint16 | 0-15 |  | N/A | See section 2.4.2.1
Nominal Active Power Limit | RRCR Power Reducer | 1 | 1 | 1 | F801 | R | - | Uint16 | 0-100 |  | % | See section 2.4.2.2
CosPhi | RRCR Power Reducer | 2 | 3 | 2 | F802 | R | - | Float32 | -1.0 - 1.0 |  | N/A | See section 2.4.2.3
Reserved | RRCR Power Reducer | 4 | 255 | 252 | F804 | - | - | - | - |  | - | Reserved
Commit Power Control Settings | Power Control - Static Settings | 0 | 0 | 1 | F900 | R/W | - | Int16 |  |  | N/A | See section 2.4.2.4 | Address Space | 1
Restore Power Control Default Settings | Power Control - Static Settings | 1 | 1 | 1 | F901 | R/W | - | Int16 |  |  | N/A | See section 2.4.2.5 | Address Offset | 2048
PwrFrqDeratingConfig | Power Control - Static Settings | 2 | 3 | 2 | F902 | R/W | + | Int32 | 0-4 |  | N/A | See section 2.4.2.6 | Category | Base Offset
ReactivePwrConfig | Power Control - Static Settings | 4 | 5 | 2 | F904 | R/W | + | Int32 | 0-4 |  | N/A | See section 2.4.2.6 | RRCR | F000
ReactPwrIterTime | Power Control - Static Settings | 6 | 7 | 2 | F906 | R/W | + | Uint32 | 0-MAX_UINT32 |  | ms | See section 2.4.2.6 | AdvPwrCtrl | F100
ActivePwrGrad | Power Control - Static Settings | 8 | 9 | 2 | F908 | R/W | + | Int32 | 0, 1 |  | N/A | See section 2.4.2.6 | Comm | F200
FixedCosPhiPhase | Power Control - Static Settings | 10 | 11 | 2 | F90A | R/W | + | Float32 | -1.0 - 1.0 |  | N/A | See section 2.4.2.6 | DynPwrCtrl | F300
FixedReactPwr | Power Control - Static Settings | 12 | 13 | 2 | F90C | R/W | + | Float32 | 0-MAX_FLOAT |  | VAR | See section 2.4.2.6 | Server | F400
ReactCosPhiVsPX[0] | Power Control - Static Settings | 14 | 15 | 2 | F90E | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6 | Storage | F500
ReactCosPhiVsPX[1] | Power Control - Static Settings | 16 | 17 | 2 | F910 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6 | PwrCtrlLimits | F600
ReactCosPhiVsPX[2] | Power Control - Static Settings | 18 | 19 | 2 | F912 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6 | EnergyControl | F700
ReactCosPhiVsPX[3] | Power Control - Static Settings | 20 | 21 | 2 | F914 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6
ReactCosPhiVsPX[4] | Power Control - Static Settings | 22 | 23 | 2 | F916 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6
ReactCosPhiVsPX[5] | Power Control - Static Settings | 24 | 25 | 2 | F918 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6
ReactCosPhiVsPY[0] | Power Control - Static Settings | 26 | 27 | 2 | F91A | R/W | + | Float32 | -1.0 - 1.0 |  | N/A | See section 2.4.2.6
ReactCosPhiVsPY[1] | Power Control - Static Settings | 28 | 29 | 2 | F91C | R/W | + | Float32 | -1.0 - 1.0 |  | N/A | See section 2.4.2.6
ReactCosPhiVsPY[2] | Power Control - Static Settings | 30 | 31 | 2 | F91E | R/W | + | Float32 | -1.0 - 1.0 |  | N/A | See section 2.4.2.6
ReactCosPhiVsPY[3] | Power Control - Static Settings | 32 | 33 | 2 | F920 | R/W | + | Float32 | -1.0 - 1.0 |  | N/A | See section 2.4.2.6
ReactCosPhiVsPY[4] | Power Control - Static Settings | 34 | 35 | 2 | F922 | R/W | + | Float32 | -1.0 - 1.0 |  | N/A | See section 2.4.2.6
ReactCosPhiVsPY[5] | Power Control - Static Settings | 36 | 37 | 2 | F924 | R/W | + | Float32 | -1.0 - 1.0 |  | N/A | See section 2.4.2.6
ReactQVsVgX[0] | Power Control - Static Settings | 38 | 39 | 2 | F926 | R/W | + | Float32 | 0-200 |  | V/Vnom % | See section 2.4.2.6
ReactQVsVgX[1] | Power Control - Static Settings | 40 | 41 | 2 | F928 | R/W | + | Float32 | 0-200 |  | V/Vnom % | See section 2.4.2.6
ReactQVsVgX[2] | Power Control - Static Settings | 42 | 43 | 2 | F92A | R/W | + | Float32 | 0-200 |  | V/Vnom % | See section 2.4.2.6
ReactQVsVgX[3] | Power Control - Static Settings | 44 | 45 | 2 | F92C | R/W | + | Float32 | 0-200 |  | V/Vnom % | See section 2.4.2.6
ReactQVsVgX[4] | Power Control - Static Settings | 46 | 47 | 2 | F92E | R/W | + | Float32 | 0-200 |  | V/Vnom % | See section 2.4.2.6
ReactQVsVgX[5] | Power Control - Static Settings | 48 | 49 | 2 | F930 | R/W | + | Float32 | 0-200 |  | V/Vnom % | See section 2.4.2.6
ReactQVsVgY[0] | Power Control - Static Settings | 50 | 51 | 2 | F932 | R/W | + | Float32 | -100 - 100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsVgY[1] | Power Control - Static Settings | 52 | 53 | 2 | F934 | R/W | + | Float32 | -100 - 100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsVgY[2] | Power Control - Static Settings | 54 | 55 | 2 | F936 | R/W | + | Float32 | -100 - 100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsVgY[3] | Power Control - Static Settings | 56 | 57 | 2 | F938 | R/W | + | Float32 | -100 - 100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsVgY[4] | Power Control - Static Settings | 58 | 59 | 2 | F93A | R/W | + | Float32 | -100 - 100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsVgY[5] | Power Control - Static Settings | 60 | 61 | 2 | F93C | R/W | + | Float32 | -100 - 100 |  | Q/Pmax % | See section 2.4.2.6
FRT_KFactor | Power Control - Static Settings | 62 | 63 | 2 | F93E | R/W | + | Float32 | 0-16 |  | N/A | See section 2.4.2.6
PowerReduce | Power Control - Static Settings | 64 | 65 | 2 | F940 | R/W | + | Float32 | 0-100 |  | % | See section 2.4.2.6
AdvancedPwrControlEn | Power Control - Static Settings | 66 | 67 | 2 | F942 | R/W | + | Int32 | 0-1 |  | N/A | See section 2.4.2.6
FrtEn | Power Control - Static Settings | 68 | 69 | 2 | F944 | R/W | + | Int32 | 0-1 |  | N/A | See section 2.4.2.6
MaxWakeupFreq | Power Control - Static Settings | 70 | 71 | 2 | F946 | R/W | + | Float32 | 0-100 |  | Hz | See section 2.4.2.6
MinWakeupFreq | Power Control - Static Settings | 72 | 73 | 2 | F948 | R/W | + | Float32 | 0-100 |  | Hz | See section 2.4.2.6
MaxWakeupVg | Power Control - Static Settings | 74 | 75 | 2 | F94A | R/W | + | Float32 | 0-500 |  | V | See section 2.4.2.6
MinWakeupVg | Power Control - Static Settings | 76 | 77 | 2 | F94C | R/W | + | Float32 | 0-500 |  | V | See section 2.4.2.6
Vnom | Power Control - Static Settings | 78 | 79 | 2 | F94E | R/W | + | Float32 | 0-500 |  | V | See section 2.4.2.6
Inom | Power Control - Static Settings | 80 | 81 | 2 | F950 | R/W | + | Float32 | 0-100 |  | A | See section 2.4.2.6
PwrVsFreqX[0] | Power Control - Static Settings | 82 | 83 | 2 | F952 | R/W | + | Float32 | 0-100 |  | Hz | See section 2.4.2.6
PwrVsFreqX[1] | Power Control - Static Settings | 84 | 85 | 2 | F954 | R/W | + | Float32 | 0-100 |  | Hz | See section 2.4.2.6
PwrVsFreqY[0] | Power Control - Static Settings | 86 | 87 | 2 | F956 | R/W | + | Float32 | 0-100 |  | % | See section 2.4.2.6
PwrVsFreqY[1] | Power Control - Static Settings | 88 | 89 | 2 | F958 | R/W | + | Float32 | 0-100 |  | % | See section 2.4.2.6
ResetFreq | Power Control - Static Settings | 90 | 91 | 2 | F95A | R/W | + | Float32 | 0-100 |  | Hz | See section 2.4.2.6
MaxFreq | Power Control - Static Settings | 92 | 93 | 2 | F95C | R/W | + | Float32 | 0-100 |  | Hz | See section 2.4.2.6
ReactQVsPX[0] | Power Control - Static Settings | 94 | 95 | 2 | F95E | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6
ReactQVsPX[1] | Power Control - Static Settings | 96 | 97 | 2 | F960 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6
ReactQVsPX[2] | Power Control - Static Settings | 98 | 99 | 2 | F962 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6
ReactQVsPX[3] | Power Control - Static Settings | 100 | 101 | 2 | F964 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6
ReactQVsPX[4] | Power Control - Static Settings | 102 | 103 | 2 | F966 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6
ReactQVsPX[5] | Power Control - Static Settings | 104 | 105 | 2 | F968 | R/W | + | Float32 | 0-100 |  | P/Pmax % | See section 2.4.2.6
ReactQVsPY[0] | Power Control - Static Settings | 106 | 107 | 2 | F96A | R/W | + | Float32 | 0-100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsPY[1] | Power Control - Static Settings | 108 | 109 | 2 | F96C | R/W | + | Float32 | 0-100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsPY[2] | Power Control - Static Settings | 110 | 111 | 2 | F96E | R/W | + | Float32 | 0-100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsPY[3] | Power Control - Static Settings | 112 | 113 | 2 | F970 | R/W | + | Float32 | 0-100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsPY[4] | Power Control - Static Settings | 114 | 115 | 2 | F972 | R/W | + | Float32 | 0-100 |  | Q/Pmax % | See section 2.4.2.6
ReactQVsPY[5] | Power Control - Static Settings | 116 | 117 | 2 | F974 | R/W | + | Float32 | 0-100 |  | Q/Pmax % | See section 2.4.2.6
PwrFrqDeratingResetTime | Power Control - Static Settings | 118 | 119 | 2 | F976 | R/W | + | Uint32 | 0-MAX_UINT32 |  | ms | See section 2.4.2.6
PwrFrqDeratingGradTime | Power Control - Static Settings | 120 | 121 | 2 | F978 | R/W | + | Uint32 | 0-MAX_UINT33 |  | ms | See section 2.4.2.6
ReactCosPhiVsPVgLockInMax | Power Control - Static Settings | 122 | 123 | 2 | F97A | R/W | + | Float32 | 0-2 |  | V/Vnom | See section 2.4.2.6
ReactCosPhiVsPVgLockInMin | Power Control - Static Settings | 124 | 125 | 2 | F97C | R/W | + | Float32 | 0-2 |  | V/Vnom | See section 2.4.2.6
ReactCosPhiVsPVgLockOutMax | Power Control - Static Settings | 126 | 127 | 2 | F97E | R/W | + | Float32 | 0-2 |  | V/Vnom | See section 2.4.2.6
ReactCosPhiVsPVgLockOutMin | Power Control - Static Settings | 128 | 129 | 2 | F980 | R/W | + | Float32 | 0-2 |  | V/Vnom | See section 2.4.2.6
ReactQVsVgPLockInMax | Power Control - Static Settings | 130 | 131 | 2 | F982 | R/W | + | Float32 | 0-1 |  | P/Pmax | See section 2.4.2.6
ReactQVsVgPLockInMin | Power Control - Static Settings | 132 | 133 | 2 | F984 | R/W | + | Float32 | 0-1 |  | P/Pmax | See section 2.4.2.6
ReactQVsVgPLockOutMax | Power Control - Static Settings | 134 | 135 | 2 | F986 | R/W | + | Float32 | 0-1 |  | P/Pmax | See section 2.4.2.6
ReactQVsVgPLockOutMin | Power Control - Static Settings | 136 | 137 | 2 | F988 | R/W | + | Float32 | 0-1 |  | P/Pmax | See section 2.4.2.6
ReactQVsVgType | Power Control - Static Settings | 138 | 139 | 2 | F98A | R/W | + | Uint32 | 0-1 |  | N/A | See section 2.4.2.6
PwrSoftStartTime | Power Control - Static Settings | 140 | 141 | 2 | F98C | R/W | + | Uint32 | 0-MAX_UINT32 |  | ms | See section 2.4.2.6
MaxCurrent | Power Control - Static Settings | 142 | 143 | 2 | F98E | R/W | + | Float32 | 0-256 |  | A | See section 2.4.2.6
Resereved | Power Control - Static Settings | 144 | 511 | 368 | F990 | - | - | Float32 |  |  |  | Reserved
ZigBee Operating Extended PAN ID | Communication | 0 | 3 | 4 | FA00 | R/W | + | Uint64 | 0-MAX_UINT64 | - | N/A | See section 2.3.2.1
ZigBee PAN ID Bank Entry 0 | Communication | 4 | 4 | 1 | FA04 | R/W | + | Uint16 | 0-MAX_UIN16 | 1AB7 | N/A | See section 2.3.2.2
ZigBee PAN ID Bank Entry 1 | Communication | 5 | 5 | 1 | FA05 | R/W | + | Uint16 | 0-MAX_UIN16 | 1AB8 | N/A | See section 2.3.2.2
ZigBee PAN ID Bank Entry 2 | Communication | 6 | 6 | 1 | FA06 | R/W | + | Uint16 | 0-MAX_UIN16 | 1AB9 | N/A | See section 2.3.2.2
ZigBee PAN ID Bank Entry 3 | Communication | 7 | 7 | 1 | FA07 | R/W | + | Uint16 | 0-MAX_UIN16 | 1ABA | N/A | See section 2.3.2.2
ZigBee PAN ID Bank Entry 4 | Communication | 8 | 8 | 1 | FA08 | R/W | + | Uint16 | 0-MAX_UIN16 | 1ABB | N/A | See section 2.3.2.2
ZigBee PAN ID Bank Entry 5 | Communication | 9 | 9 | 1 | FA09 | R/W | + | Uint16 | 0-MAX_UIN16 | 1ABC | N/A | See section 2.3.2.2
ZigBee PAN ID Bank Entry 6 | Communication | 10 | 10 | 1 | FA0A | R/W | + | Uint16 | 0-MAX_UIN16 | 1ABD | N/A | See section 2.3.2.2
ZigBee PAN ID Bank Entry 7 | Communication | 11 | 11 | 1 | FA0B | R/W | + | Uint16 | 0-MAX_UIN16 | 1ABE | N/A | See section 2.3.2.2
ZigBee PAN ID Bank Entry 8 | Communication | 12 | 12 | 1 | FA0C | R/W | + | Uint16 | 0-MAX_UIN16 | 1ABF | N/A | See section 2.3.2.2
ZigBee PAN ID Bank Entry 9 | Communication | 13 | 13 | 1 | FA0D | R/W | + | Uint16 | 0-MAX_UIN16 | 1AC0 | N/A | See section 2.3.2.2
Server Load Control | Communication | 14 | 14 | 1 | FA0E | R/W | + | Uint16 | 0-2 | 1 | N/A | See section 2.3.2.3
ZigBee PAN Hop Control | Communication | 15 | 15 | 1 | FA0F | R/W | + | Uint16 | 0-1 | 0 | N/A | See section 2.3.2.4
ZigBee Options | Communication | 16 | 16 | 1 | FA10 | R | + | Uint16 | 0-1 | 0 | N/A | 0 - Default; 1 - PAN Hoping Mode
ZigBee RSSI | Communication | 17 | 17 | 1 | FA11 | R | - | Int16 |  | - | dBm
ZigBee LQI | Communication | 18 | 18 | 1 | FA12 | R | - | Uint16 | 0-FF | - | N/A
Enable Dynamic Power Control | Power Control - Dynamic Settings | 0 | 0 | 1 | FB00 | R/W | + | Uint16 | 0-1 | 0 | N/A | See section 3
Resereved | Power Control - Dynamic Settings | 1 | 1 | 1 | FB01 | R | - | Uint16 | - | - | - | Reserved
Max Apparent Power | Power Control - Dynamic Settings | 2 | 3 | 2 | FB02 | R | - | Float32 | According to inverter rating |  | VA | See section 3
Max Active Power | Power Control - Dynamic Settings | 4 | 5 | 2 | FB04 | R | - | Float32 | According to inverter rating |  | W | See section 3
Max Reactive Power | Power Control - Dynamic Settings | 6 | 7 | 2 | FB06 | R | - | Float32 | According to inverter rating |  | VAR | See section 3
Active/Reactive Preference | Power Control - Dynamic Settings | 8 | 8 | 1 | FB08 | R/W | + | Uint16 | 0-1 | 0 | 0-1 | See section 3
CosPhi/Q Preference | Power Control - Dynamic Settings | 9 | 9 | 1 | FB09 | R/W | + | Uint16 | 0-1 | 0 | 0-1 | See section 3
Apparent Power Limit | Power Control - Dynamic Settings | 10 | 11 | 2 | FB0A | R/W | + | Float32 | According to inverter rating |  | VA | See section 3
Active Power Limit | Power Control - Dynamic Settings | 12 | 13 | 2 | FB0C | R/W | + | Float32 | According to inverter rating |  | W | See section 3
Reactive Power Limit | Power Control - Dynamic Settings | 14 | 15 | 2 | FB0E | R/W | + | Float32 | According to inverter rating |  | VAR | See section 3
Command Timeout | Power Control - Dynamic Settings | 16 | 17 | 2 | FB10 | R/W | + | Uint32 | 0-MAX_UINT32 | 60 | Sec | See section 3
Fallback Active Power Limit | Power Control - Dynamic Settings | 18 | 19 | 2 | FB12 | R/W | + | Float32 |  | 100 | % | See section 3
Fallback Reactive Power Limit | Power Control - Dynamic Settings | 20 | 21 | 2 | FB14 | R/W | + | Float32 |  | 0 | % | See section 3
Fallback CosPhi | Power Control - Dynamic Settings | 22 | 23 | 2 | FB16 | R/W | + | Float32 |  | 1 | N/A | See section 3
Active Power Ramp-up Rate | Power Control - Dynamic Settings | 24 | 25 | 2 | FB18 | R/W | + | Float32 |  | 5 | %/min | See section 3
Active Power Ramp-down Rate | Power Control - Dynamic Settings | 26 | 27 | 2 | FB1A | R/W | + | Float32 |  | 5 | %/min | See section 3
Rective Power Ramp-up Rate | Power Control - Dynamic Settings | 28 | 29 | 2 | FB1C | R/W | + | Float32 |  | 5 | %/min | See section 3
Reactive Power Ramp-down Rate | Power Control - Dynamic Settings | 30 | 31 | 2 | FB1E | R/W | + | Float32 |  | 5 | %/min | See section 3
Phi Change Rate | Power Control - Dynamic Settings | 32 | 33 | 2 | FB20 | R/W | + | Float32 |  | Pi/2 | rad/min | See section 3
Dynamic Active Power Limit | Power Control - Dynamic Settings | 34 | 35 | 2 | FB22 | R/W | - | Float32 | - | - | % | See section 3
Dynamic Reactive Power Ref | Power Control - Dynamic Settings | 36 | 37 | 2 | FB24 | R/W | - | Float32 | - | - | % | See section 3
Dynamic CosPhi Ref | Power Control - Dynamic Settings | 38 | 39 | 2 | FB26 | R/W | - | Float32 | - | - | N/A | See section 3
ReadDataSize | ServerStream | 0 | 0 | 1 | FC00 | R | - | UInt16 | - | - | Bytes
ReadData | ServerStream | 1 | 1 | 1 | FC01 | R | - | Byte[] | - | - | -
WriteData | ServerStream | 1 | 1 | 1 | FC02 | W | - | Byte[] | - | - | -
Manufacturer | Storage Device Info | 0 | 15 | 16 | FD00 | R | - | String[32] |  | - | -
Model | Storage Device Info | 16 | 31 | 16 | FD10 | R | - | String[32] |  | - | -
Version | Storage Device Info | 32 | 47 | 16 | FD20 | R | - | String[32] |  | - | -
SerialNumber | Storage Device Info | 48 | 63 | 16 | FD30 | R | - | String[32] |  | - | -
DeviceAddress | Storage Device Info | 64 | 64 | 1 | FD40 | R | - | Uint16 |  | - | -
Reserved | Storage Device Info | 65 | 65 | 1 | FD41 | R | - | Uint16 |  | - | -
Rated Energy | Storage Device Info | 66 | 67 | 2 | FD42 | R | - | Float32 |  | - | W*H
Max Charge Power | Storage Device Info | 68 | 69 | 2 | FD44 | R | - | Float32 |  | - | W
Max Discharge Power | Storage Device Info | 70 | 71 | 2 | FD46 | R | - | Float32 |  | - | W
Max Charge Surge Power | Storage Device Info | 72 | 73 | 2 | FD48 | R | - | Float32 |  | - | W
Max Discharge Surge Power | Storage Device Info | 74 | 75 | 2 | FD4A | R | - | Float32 |  | - | W
Reserved | Storage Device Info | 76 | 107 | 32 | FD4C | R | - | Uint16 |  | - | -
Avg Temperature | Storage Device Status | 108 | 109 | 2 | FD6C | R | - | Float32 |  | - | °C
Max Temperature | Storage Device Status | 110 | 111 | 2 | FD6E | R | - | Float32 |  | - | °C
Voltage | Storage Device Status | 112 | 113 | 2 | FD70 | R | - | Float32 |  | - | V
Current | Storage Device Status | 114 | 115 | 2 | FD72 | R | - | Float32 |  | - | A
Power | Storage Device Status | 116 | 117 | 2 | FD74 | R | - | Float32 |  | - | W
LifeTime Export | Storage Device Status | 118 | 121 | 4 | FD76 | R | - | Uint64 |  | - | W*H
LifeTime Import | Storage Device Status | 122 | 125 | 4 | FD7A | R | - | Uint64 |  | - | W*H
Max Energy | Storage Device Status | 126 | 127 | 2 | FD7E | R | - | Float32 |  | - | W*H | SOH = MaxEnergy\RatedEnergy
Available Energy | Storage Device Status | 128 | 129 | 2 | FD80 | R | - | Float32 |  | - | W*H | SOE = AvailableEnergy\MaxEnergy
SOH | Storage Device Status | 130 | 131 | 2 | FD82 | R | - | Float32 |  | - | N/A
SOE | Storage Device Status | 132 | 133 | 2 | FD84 | R | - | Float32 |  | - | N/A
Status | Storage Device Status | 134 | 135 | 2 | FD86 | R | - | Uint32 |  | - | enum | 0 - Off 1 - Standby 2 - Init 3 - Charge 4 - Discharge 5 - Fault 6 - Idle
Status Internal | Storage Device Status | 136 | 137 | 2 | FD88 | R | - | Uint32 |  | - | enum
Events Log | Storage Device Status | 138 | 145 | 8 | FD8A | R | - | Uint16[8] |  | - | enum | EventsLog[0] - Battery vendor's fault ID
Events Log Internal | Storage Device Status | 146 | 153 | 8 | FD92 | R | - | Uint16[8] |  | - | enum
Reserved | Storage Device Status | 154 | 185 | 32 | FD9A | R | - | Uint16 |  | - | N/A
Commit Limit Settings | Power Control - Trips Settings | 0 | 0 | 1 | FE00 | R/W | - | Int16 |  |  |  | Commit latest changes to apply changes
Restore Limit Settings Defaults | Power Control - Trips Settings | 1 | 1 | 1 | FE01 | R/W | - | Int16 |  |  |  | Restores settings to grid defaults
VgMax1 | Power Control - Trips Settings | 2 | 3 | 2 | FE02 | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMax1_HoldTime | Power Control - Trips Settings | 4 | 5 | 2 | FE04 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
VgMax2 | Power Control - Trips Settings | 6 | 7 | 2 | FE06 | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMax2_HoldTime | Power Control - Trips Settings | 8 | 9 | 2 | FE08 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
VgMax3 | Power Control - Trips Settings | 10 | 11 | 2 | FE0A | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMax3_HoldTime | Power Control - Trips Settings | 12 | 13 | 2 | FE0C | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
VgMax4 | Power Control - Trips Settings | 14 | 15 | 2 | FE0E | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMax4_HoldTime | Power Control - Trips Settings | 16 | 17 | 2 | FE10 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
VgMax5 | Power Control - Trips Settings | 18 | 19 | 2 | FE12 | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMax5_HoldTime | Power Control - Trips Settings | 20 | 21 | 2 | FE14 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
VgMin1 | Power Control - Trips Settings | 22 | 23 | 2 | FE16 | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMin1_HoldTime | Power Control - Trips Settings | 24 | 25 | 2 | FE18 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
VgMin2 | Power Control - Trips Settings | 26 | 27 | 2 | FE1A | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMin2_HoldTime | Power Control - Trips Settings | 28 | 29 | 2 | FE1C | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
VgMin3 | Power Control - Trips Settings | 30 | 31 | 2 | FE1E | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMin3_HoldTime | Power Control - Trips Settings | 32 | 33 | 2 | FE20 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
VgMin4 | Power Control - Trips Settings | 34 | 35 | 2 | FE22 | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMin4_HoldTime | Power Control - Trips Settings | 36 | 37 | 2 | FE24 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
VgMin5 | Power Control - Trips Settings | 38 | 39 | 2 | FE26 | R/W | + | Float32 | 0-MAX_FLOAT |  | V | Initial value according to selected grid default
VgMin5_HoldTime | Power Control - Trips Settings | 40 | 41 | 2 | FE28 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMax1 | Power Control - Trips Settings | 42 | 43 | 2 | FE2A | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMax1_HoldTime | Power Control - Trips Settings | 44 | 45 | 2 | FE2C | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMax2 | Power Control - Trips Settings | 46 | 47 | 2 | FE2E | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMax2_HoldTime | Power Control - Trips Settings | 48 | 49 | 2 | FE30 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMax3 | Power Control - Trips Settings | 50 | 51 | 2 | FE32 | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMax3_HoldTime | Power Control - Trips Settings | 52 | 53 | 2 | FE34 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMax4 | Power Control - Trips Settings | 54 | 55 | 2 | FE36 | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMax4_HoldTime | Power Control - Trips Settings | 56 | 57 | 2 | FE38 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMax5 | Power Control - Trips Settings | 58 | 59 | 2 | FE3A | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMax5_HoldTime | Power Control - Trips Settings | 60 | 61 | 2 | FE3C | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMin1 | Power Control - Trips Settings | 62 | 63 | 2 | FE3E | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMin1_HoldTime | Power Control - Trips Settings | 64 | 65 | 2 | FE40 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMin2 | Power Control - Trips Settings | 66 | 67 | 2 | FE42 | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMin2_HoldTime | Power Control - Trips Settings | 68 | 69 | 2 | FE44 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMin3 | Power Control - Trips Settings | 70 | 71 | 2 | FE46 | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMin3_HoldTime | Power Control - Trips Settings | 72 | 73 | 2 | FE48 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMin4 | Power Control - Trips Settings | 74 | 75 | 2 | FE4A | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMin4_HoldTime | Power Control - Trips Settings | 76 | 77 | 2 | FE4C | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
FgMin5 | Power Control - Trips Settings | 78 | 79 | 2 | FE4E | R/W | + | Float32 | 0-MAX_FLOAT |  | Hz | Initial value according to selected grid default
FgMin5_HoldTime | Power Control - Trips Settings | 80 | 81 | 2 | FE50 | R/W | + | Uint32 | 0-MAX_UINT32 |  | msec | Initial value according to selected grid default
GrmTime | Power Control - Trips Settings | 82 | 83 | 2 | FE52 | R/W | + | Uint32 | 0-MAX_FLOAT |  | msec | Initial value according to selected grid default
ExportConf_Ctrl | Energy Control - Limit Configuration | 0 | 0 | 1 | FF00 | R/W | + | Uint16 | Bits 0 (LSB) - 11 |  | BitField | Control Mode (Single selection allowed): All bits off - Disabled Bit 0 on - Direct Export Limitation (via export meter) Bit 1 on - In-direct Export Limitation (via consumption meter) Bit 2 on - Production Limitation (via production meter Options (Multiple Selection allowed): Bit 10 on - External Production Bit 11 on - Negative Site Limit Example, Direct Export Limitation with Negative site limit: 0000100000000001
ExportConf_LimitMode | Energy Control - Limit Configuration | 1 | 1 | 1 | FF01 | R/W | + | Uint16 | 0-1 |  | Enum | 0 - Total 1 - PerPhase
ExportConf_SiteLimit | Energy Control - Limit Configuration | 2 | 3 | 2 | FF02 | R/W | + | Float32 | 0-MAX_FLOAT |  | W | Site limit in Watts
StorageConf_CtrlMode | Energy Control - Storage Configuration | 0 | 0 | 1 | FF04 | R/W | + | Uint16 | 0-4 |  | Enum | 0 - Disabled 1 - MSC 2 - TOU 3 - BackupOnly 4 - Remote Notice that advanced power control such as MaxP(V) or gradients run in parallel and have priority
StorageConf_AcChargePolicy | Energy Control - Storage Configuration | 1 | 1 | 1 | FF05 | R/W | + | Uint16 | 0-3 |  | Enum | 0 - Disable 1 - AlwaysAllowed 2 - FixedLimitWatt 3 - Percent of Production
StorageConf_AcChargeLimit | Energy Control - Storage Configuration | 2 | 3 | 2 | FF06 | R/W | + | Float32 | 0-MAX_FLOAT |  | KW or % | According to prev register (e.g. 100KW or 70%)
StorageConf_BackupReserved | Energy Control - Storage Configuration | 4 | 5 | 2 | FF08 | R/W | + | Float32 | 0-100 |  | % | Percent of storage system SOE to reserve for backup purposes
StorageConf_DefaultMode | Energy Control - Storage Configuration | 6 | 6 | 1 | FF0A | R/W | + | Uint16 | 0-7 |  | Enum | Enum StorageCtrlMode: 0 - Off 1 - Charge excess PV 2 - Charge all from PV 3 - Charge all from PV+AC 4 - Maximize export 5 - Discharge to meet loads 7 - Maximize self-consumption * Modes 5 and 7 require an external consumption/export meter
StorageRemoteCtrl_CommandTimeout | Energy Control - Storage Remote Control | 7 | 8 | 2 | FF0B | R/W | - | Uint32 | 0-86400(24h) |  | Sec | The time before reverting back to default mode
StorageRemoteCtrl_CommandMode | Energy Control - Storage Remote Control | 13 | 13 | 1 | FF0D | R/W | - | Uint16 | 0-7 |  | Enum | According to StorageCtrlMode enum
StorageRemoteCtrl_ChargeLimit | Energy Control - Storage Remote Control | 14 | 15 | 2 | FF0E | R/W | - | Float32 | 0-MAX_FLOAT |  | W | Sets the max charge limit
StorageRemoteCtrl_DischargeLimit | Energy Control - Storage Remote Control | 16 | 17 | 2 | FF10 | R/W | - | Float32 | 0-MAX_FLOAT |  | W | Sets the max discharge limit
MSC_Month1OnHour | Energy Control - MSC Table | TBD | [9 empty] | The time in min from 0:00 where MSC actives during Jan
MSC_Month1OffHour | Energy Control - MSC Table | TBD | [9 empty] | The time in min from 0:00 where MSC disables during Jan
MSC_Month2OnHour | Energy Control - MSC Table | TBD | [9 empty] | …
MSC_Month2OffHour | Energy Control - MSC Table | TBD
… | Energy Control - MSC Table | TBD
MSC_Month12OnHour | Energy Control - MSC Table | TBD
MSC_Month12OffHour | Energy Control - MSC Table | TBD
MSC_Reserved | Energy Control - MSC Table | TBD
MSB-LSB
LSB-MSB
Address Space

## SEM_Registers
Label | Category | Start | End | Size | Address | Access Level | NV | Type | Range | Default | Units | Description
ExportConf_Ctrl | Energy Control - Limit Configuration | 0 | 0 | 1 | E800 | R/W | + | Uint16 | Bits 0 (LSB) - 11 |  | BitField | Control Mode (Single selection allowed): All bits off - Disabled Bit 0 on - Direct Export Limitation (via export meter) Bit 1 on - In-direct Export Limitation (via consumption meter) Bit 2 on - Production Limitation (via production meter Options (Multiple Selection allowed): Bit 10 on - External Production Bit 11 on - Negative Site Limit Example, Direct Export Limitation with Negative site limit: 0000100000000001
ExportConf_LimitMode | Energy Control - Limit Configuration | 1 | 1 | 1 | E801 | R/W | + | Uint16 | 0-1 |  | Enum | 0 - Total 1 - PerPhase
ExportConf_SiteLimit | Energy Control - Limit Configuration | 2 | 3 | 2 | E802 | R/W | + | Float32 | 0-MAX_FLOAT |  | W | Site limit in Watts
StorageConf_CtrlMode | Energy Control - Storage Configuration | 6 | 6 | 1 | E804 | R/W | + | Uint16 | 0-4 |  | Enum | 0 - Disabled 1 - MSC 2 - TOU 3 - BackupOnly 4 - Remote Notice that advanced power control such as MaxP(V) or gradients run in parallel and have priority
StorageConf_AcChargePolicy | Energy Control - Storage Configuration | 7 | 7 | 1 | E805 | R/W | + | Uint16 | 0-3 |  | Enum | 0 - Disable 1 - AlwaysAllowed 2 - FixedLimitWatt 3 - Percent of Production
StorageConf_AcChargeLimit | Energy Control - Storage Configuration | 8 | 9 | 2 | E806 | R/W | + | Float32 | 0-MAX_FLOAT |  | KW or % | According to prev register (e.g. 100KW or 70%)
StorageConf_BackupReserved | Energy Control - Storage Configuration | 10 | 11 | 2 | E808 | R/W | + | Float32 | 0-100 |  | % | Percent of storage system SOE to reserve for backup purposes
StorageConf_DefaultMode | Energy Control - Storage Configuration | 12 | 12 | 1 | E80A | R/W | + | Uint16 | 0-7 |  | Enum | Enum StorageCtrlMode: 0 - Off 1 - Charge excess PV 2 - Charge all from PV 3 - Charge all from PV+AC 4 - Maximize export 5 - Discharge to meet loads 7 - Maximize self-consumption * Modes 5 and 7 require an external consumption/export meter
StorageRemoteCtrl_CommandTimeout | Energy Control - Storage Remote Control | 13 | 14 | 2 | E80B | R/W | - | Uint32 | 0-86400(24h) |  | Sec | The time before reverting back to default mode | Address Space | 1
StorageRemoteCtrl_CommandMode | Energy Control - Storage Remote Control | 13 | 13 | 1 | E80D | R/W | - | Uint16 | 0-7 |  | Enum | According to StorageCtrlMode enum | Address Offset | 2048
StorageRemoteCtrl_ChargeLimit | Energy Control - Storage Remote Control | 14 | 15 | 2 | E80E | R/W | - | Float32 | 0-MAX_FLOAT |  | W | Sets the max charge limit | Category | Base Offset
StorageRemoteCtrl_DischargeLimit | Energy Control - Storage Remote Control | 16 | 17 | 2 | E810 | R/W | - | Float32 | 0-MAX_FLOAT |  | W | Sets the max discharge limit | Energy Control | E000
ExportConf_ExternalProdMaxPower | Energy Control - Adv. Limit Configuration | 4 | 5 | 2 | E812 | R/W | + | Float32 | 0-MAX_FLOAT |  | W | External Production Max Power | Storage Device 1 | E100
Manufacturer | Storage Device 1 Info | 0 | 15 | 16 | E900 | R | - | String[32] |  | - | - |  | Storage Device 2 | E200
Model | Storage Device 1 Info | 16 | 31 | 16 | E910 | R | - | String[32] |  | - | -
Version | Storage Device 1 Info | 32 | 47 | 16 | E920 | R | - | String[32] |  | - | -
SerialNumber | Storage Device 1 Info | 48 | 63 | 16 | E930 | R | - | String[32] |  | - | -
DeviceAddress | Storage Device 1 Info | 64 | 64 | 1 | E940 | R | - | Uint16 |  | - | -
Reserved | Storage Device 1 Info | 65 | 65 | 1 | E941 | R | - | Uint16 |  | - | -
Rated Energy | Storage Device 1 Info | 66 | 67 | 2 | E942 | R | - | Float32 |  | - | W*H
Max Charge Power | Storage Device 1 Info | 68 | 69 | 2 | E944 | R | - | Float32 |  | - | W
Max Discharge Power | Storage Device 1 Info | 70 | 71 | 2 | E946 | R | - | Float32 |  | - | W
Max Charge Surge Power | Storage Device 1 Info | 72 | 73 | 2 | E948 | R | - | Float32 |  | - | W
Max Discharge Surge Power | Storage Device 1 Info | 74 | 75 | 2 | E94A | R | - | Float32 |  | - | W
Reserved | Storage Device 1 Info | 76 | 107 | 32 | E94C | R | - | Uint16 |  | - | -
Avg Temperature | Storage Device 1 Status | 108 | 109 | 2 | E96C | R | - | Float32 |  | - | °C
Max Temperature | Storage Device 1 Status | 110 | 111 | 2 | E96E | R | - | Float32 |  | - | °C
Voltage | Storage Device 1 Status | 112 | 113 | 2 | E970 | R | - | Float32 |  | - | V
Current | Storage Device 1 Status | 114 | 115 | 2 | E972 | R | - | Float32 |  | - | A
Power | Storage Device 1 Status | 116 | 117 | 2 | E974 | R | - | Float32 |  | - | W
LifeTime Export | Storage Device 1 Status | 118 | 121 | 4 | E976 | R | - | Uint64 |  | - | W*H
LifeTime Import | Storage Device 1 Status | 122 | 125 | 4 | E97A | R | - | Uint64 |  | - | W*H
Max Energy | Storage Device 1 Status | 126 | 127 | 2 | E97E | R | - | Float32 |  | - | W*H | SOH = MaxEnergy\RatedEnergy
Available Energy | Storage Device 1 Status | 128 | 129 | 2 | E980 | R | - | Float32 |  | - | W*H | SOE = AvailableEnergy\MaxEnergy
SOH | Storage Device 1 Status | 130 | 131 | 2 | E982 | R | - | Float32 |  | - | N/A
SOE | Storage Device 1 Status | 132 | 133 | 2 | E984 | R | - | Float32 |  | - | N/A
Status | Storage Device 1 Status | 134 | 135 | 2 | E986 | R | - | Uint32 |  | - | enum | 0 - Off 1 - Standby 2 - Init 3 - Charge 4 - Discharge 5 - Fault 7 - Idle
Status Internal | Storage Device 1 Status | 136 | 137 | 2 | E988 | R | - | Uint32 |  | - | enum
Events Log | Storage Device 1 Status | 138 | 145 | 8 | E98A | R | - | Uint16[8] |  | - | enum | EventsLog[0] - Battery vendor's fault ID
Events Log Internal | Storage Device 1 Status | 146 | 153 | 8 | E992 | R | - | Uint16[8] |  | - | enum
Reserved | Storage Device 1 Status | 154 | 185 | 32 | E99A | R | - | Uint16 |  | - | N/A
Manufacturer | Storage Device 2 Info | 0 | 15 | 16 | EA00 | R | - | String[32] |  | - | -
Model | Storage Device 2 Info | 16 | 31 | 16 | EA10 | R | - | String[32] |  | - | -
Version | Storage Device 2 Info | 32 | 47 | 16 | EA20 | R | - | String[32] |  | - | -
SerialNumber | Storage Device 2 Info | 48 | 63 | 16 | EA30 | R | - | String[32] |  | - | -
DeviceAddress | Storage Device 2 Info | 64 | 64 | 1 | EA40 | R | - | Uint16 |  | - | -
Reserved | Storage Device 2 Info | 65 | 65 | 1 | EA41 | R | - | Uint16 |  | - | -
Rated Energy | Storage Device 2 Info | 66 | 67 | 2 | EA42 | R | - | Float32 |  | - | W*H
Max Charge Power | Storage Device 2 Info | 68 | 69 | 2 | EA44 | R | - | Float32 |  | - | W
Max Discharge Power | Storage Device 2 Info | 70 | 71 | 2 | EA46 | R | - | Float32 |  | - | W
Max Charge Surge Power | Storage Device 2 Info | 72 | 73 | 2 | EA48 | R | - | Float32 |  | - | W
Max Discharge Surge Power | Storage Device 2 Info | 74 | 75 | 2 | EA4A | R | - | Float32 |  | - | W
Reserved | Storage Device 2 Info | 76 | 107 | 32 | EA4C | R | - | Uint16 |  | - | -
Avg Temperature | Storage Device 2 Status | 108 | 109 | 2 | EA6C | R | - | Float32 |  | - | °C
Max Temperature | Storage Device 2 Status | 110 | 111 | 2 | EA6E | R | - | Float32 |  | - | °C
Voltage | Storage Device 2 Status | 112 | 113 | 2 | EA70 | R | - | Float32 |  | - | V
Current | Storage Device 2 Status | 114 | 115 | 2 | EA72 | R | - | Float32 |  | - | A
Power | Storage Device 2 Status | 116 | 117 | 2 | EA74 | R | - | Float32 |  | - | W
LifeTime Export | Storage Device 2 Status | 118 | 121 | 4 | EA76 | R | - | Uint64 |  | - | W*H
LifeTime Import | Storage Device 2 Status | 122 | 125 | 4 | EA7A | R | - | Uint64 |  | - | W*H
Max Energy | Storage Device 2 Status | 126 | 127 | 2 | EA7E | R | - | Float32 |  | - | W*H | SOH = MaxEnergy\RatedEnergy
Available Energy | Storage Device 2 Status | 128 | 129 | 2 | EA80 | R | - | Float32 |  | - | W*H | SOE = AvailableEnergy\MaxEnergy
SOH | Storage Device 2 Status | 130 | 131 | 2 | EA82 | R | - | Float32 |  | - | N/A
SOE | Storage Device 2 Status | 132 | 133 | 2 | EA84 | R | - | Float32 |  | - | N/A
Status | Storage Device 2 Status | 134 | 135 | 2 | EA86 | R | - | Uint32 |  | - | enum | 0 - Off 1 - Standby 2 - Init 3 - Charge 4 - Discharge 5 - Fault 7 - Idle
Status Internal | Storage Device 2 Status | 136 | 137 | 2 | EA88 | R | - | Uint32 |  | - | enum
Events Log | Storage Device 2 Status | 138 | 145 | 8 | EA8A | R | - | Uint16[8] |  | - | enum | EventsLog[0] - Battery vendor's fault ID
Events Log Internal | Storage Device 2 Status | 146 | 153 | 8 | EA92 | R | - | Uint16[8] |  | - | enum
Reserved | Storage Device 2 Status | 154 | 185 | 32 | EA9A | R | - | Uint16 |  | - | N/A
MSB-LSB
LSB-MSB
Address Space